Load Carrying Capacities (see table below) http://www.powerstream.com/Wire_Size.htm
The following chart is a guideline of ampacity or copper wire current carrying capacity following the Handbook of Electronic Tables and Formulas for American Wire Gauge. As you might guess, the rated ampacities are just a rule of thumb. In careful engineering the voltage drop, insulation temperature limit, thickness, thermal conductivity, and air convection and temperature 綁線 絕緣纜線 should all be taken into account. The Maximum Amps for Power Transmission uses the 700 circular mils per amp rule, which is very very conservative 適用於 變壓器線圈內纏繞線團. The Maximum Amps for Chassis Wiring is also a conservative rating, but is meant for wiring in air裸線, and not in a bundle. For short lengths of wire, such as is used in battery packs you should trade off the resistance and load with size, weight, and flexibility.

| AWG gauge | Conductor Diameter Inches | Conductor Diameter mm | Ohms per 1000 ft | Ohms per km | Maximum amps for chassis wiring 裸線 | Maximum amps for power transmission | Maximum freqency for 100% skin depth for solid conductor copper |
| --- | --- | --- | --- | --- | --- | --- | --- |
| OOOO | 0.46 | 11.684 | 0.049 | 0.16072 | 380 | 302 | 125 Hz |
| OOO | 0.4096 | 10.40384 | 0.0618 | 0.202704 | 328 | 239 | 160 Hz |
| OO | 0.3648 | 9.26592 | 0.0779 | 0.255512 | 283 | 190 | 200 Hz |
| 0 | 0.3249 | 8.25246 | 0.0983 | 0.322424 | 245 | 150 | 250 Hz |
| 1 | 0.2893 | 7.34822 | 0.1239 | 0.406392 | 211 | 119 | 325 Hz |
| 2 | 0.2576 | 6.54304 | 0.1563 | 0.512664 | 181 | 94 | 410 Hz |
| 3 | 0.2294 | 5.82676 | 0.197 | 0.64616 | 158 | 75 | 500 Hz |
| 4 | 0.2043 | 5.18922 | 0.2485 | 0.81508 | 135 | 60 | 650 Hz |
| 5 | 0.1819 | 4.62026 | 0.3133 | 1.027624 | 118 | 47 | 810 Hz |
| 6 | 0.162 | 4.1148 | 0.3951 | 1.295928 | 101 | 37 | 1100 Hz |
| 7 | 0.1443 | 3.66522 | 0.4982 | 1.634096 | 89 | 30 | 1300 Hz |
| 8 | 0.1285 | 3.2639 | 0.6282 | 2.060496 | 73 | 24 | 1650 Hz |
| 9 | 0.1144 | 2.90576 | 0.7921 | 2.598088 | 64 | 19 | 2050 Hz |
| 10 | 0.1019 | 2.58826 | 0.9989 | 3.276392 | 55 | 15 | 2600 Hz |
| 11 | 0.0907 | 2.30378 | 1.26 | 4.1328 | 47 | 12 | 3200 Hz |
| 12 | 0.0808 | 2.05232 | 1.588 | 5.20864 | 41 | 9.3 | 4150 Hz |
| 13 | 0.072 | 1.8288 | 2.003 | 6.56984 | 35 | 7.4 | 5300 Hz |
| 14 | 0.0641 | 1.62814 | 2.525 | 8.282 | 32 | 5.9 | 6700 Hz |
| 15 | 0.0571 | 1.45034 | 3.184 | 10.44352 | 28 | 4.7 | 8250 Hz |
| 16 | 0.0508 | 1.29032 | 4.016 | 13.17248 | 22 | 3.7 | 11 k Hz |
| 17 | 0.0453 | 1.15062 | 5.064 | 16.60992 | 19 | 2.9 | 13 k Hz |
| 18 | 0.0403 | 1.02362 | 6.385 | 20.9428 | 16 | 2.3 | 17 kHz |
| 19 | 0.0359 | 0.91186 | 8.051 | 26.40728 | 14 | 1.8 | 21 kHz |
| 20 | 0.032 | 0.8128 | 10.15 | 33.292 | 11 | 1.5 | 27 kHz |
| 21 | 0.0285 | 0.7239 | 12.8 | 41.984 | 9 | 1.2 | 33 kHz |
| 22 | 0.0254 | 0.64516 | 16.14 | 52.9392 | 7 | 0.92 | 42 kHz |
| 23 | 0.0226 | 0.57404 | 20.36 | 66.7808 | 4.7 | 0.729 | 53 kHz |
| 24 | 0.0201 | 0.51054 | 25.67 | 84.1976 | 3.5 | 0.577 | 68 kHz |
| 25 | 0.0179 | 0.45466 | 32.37 | 106.1736 | 2.7 | 0.457 | 85 kHz |
| 26 | 0.0159 | 0.40386 | 40.81 | 133.8568 | 2.2 | 0.361 | 107 kH |
| 27 | 0.0142 | 0.36068 | 51.47 | 168.8216 | 1.7 | 0.288 | 130 kHz |
| 28 | 0.0126 | 0.32004 | 64.9 | 212.872 | 1.4 | 0.226 | 170 kHz |
| 29 | 0.0113 | 0.28702 | 81.83 | 268.4024 | 1.2 | 0.182 | 210 kHz |
| 30 | 0.01 | 0.254 | 103.2 | 338.496 | 0.86 | 0.142 | 270 kHz |
| 31 | 0.0089 | 0.22606 | 130.1 | 426.728 | 0.7 | 0.113 | 340 kHz |
| 32 | 0.008 | 0.2032 | 164.1 | 538.248 | 0.53 | 0.091 | 430 kHz |
| Metric 2.0 | 0.00787 | 0.200 | 169.39 | 555.61 | 0.51 | 0.088 | 440 kHz |
| 33 | 0.0071 | 0.18034 | 206.9 | 678.632 | 0.43 | 0.072 | 540 kHz |
| Metric 1.8 | 0.00709 | 0.180 | 207.5 | 680.55 | 0.43 | 0.072 | 540 kHz |
| 34 | 0.0063 | 0.16002 | 260.9 | 855.752 | 0.33 | 0.056 | 690 kHz |
| Metric 1.6 | 0.0063 | 0.16002 | 260.9 | 855.752 | 0.33 | 0.056 | 690 kHz |
| 35 | 0.0056 | 0.14224 | 329 | 1079.12 | 0.27 | 0.044 | 870 kHz |
| Metric 1.4 | .00551 | .140 | 339 | 1114 | 0.26 | 0.043 | 900 kHz |
| 36 | 0.005 | 0.127 | 414.8 | 1360 | 0.21 | 0.035 | 1100 kHz |
| Metric 1.25 | .00492 | 0.125 | 428.2 | 1404 | 0.20 | 0.034 | 1150 kHz |
| 37 | 0.0045 | 0.1143 | 523.1 | 1715 | 0.17 | 0.0289 | 1350 kHz |
| Metric 1.12 | .00441 | 0.112 | 533.8 | 1750 | 0.163 | 0.0277 | 1400 kHz |
| 38 | 0.004 | 0.1016 | 659.6 | 2163 | 0.13 | 0.0228 | 1750 kHz |
| Metric 1 | .00394 | 0.1000 | 670.2 | 2198 | 0.126 | 0.0225 | 1750 kHz |
| 39 | 0.0035 | 0.0889 | 831.8 | 2728 | 0.11 | 0.0175 | 2250 kHz |
| 40 | 0.0031 | 0.07874 | 1049 | 3440 | 0.09 | 0.0137 | 2900 kHz |

Reade Advanced Materials presents: Wire Gauge / Gage Conversion Chart http://www.reade.com/Conversion/wire_gauge.html

| S.W.G. | Wire Number | A.W.G. or B&S | A.W.G. Metric |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (Inches) | (Gauge) | (Inches) | (MM) |  |  |  |  |
| 0.500 | 0000000 (7/0) | ....................... | ............ |  |  |  |  |
| 0.464 | 000000 (6/0) | 0.580000 | ............ |  |  |  |  |
| 0.432 | 00000 (5/0) | 0.516500 | ............ |  |  |  |  |
| 0.400 | 0000 (4/0) | 0.460000 | 11,684 | 0.0164 | 27 | 0.0142 | 0,3606 |
| 0.372 | 000 (3/0) | 0.409642 | 10,404 | 0.0148 | 28 | 0.0126 | 0,3200 |
| 0.348 | 00 (2/0) | 0.364796 | 9,266 | 0.0136 | 29 | 0.0113 | 0,2870 |
| 0.324 | 0 (1/0) | 0.324861 | 8,252 | 0.0124 | 30 | 0.0100 | 0,2540 |
| 0.300 | 1 | 0.289297 | 7,348 | 0.0116 | 31 | 0.0089 | 0,2261 |
| 0.276 | 2 | 0.257627 | 6,543 | 0.0108 | 32 | 0.0080 | 0,2032 |
| 0.252 | 3 | 0.229423 | 5,827 | 0.0100 | 33 | 0.0071 | 0,1803 |
| 0.232 | 4 | 0.2043 | 5,189 | S.W.G. | Wire Number | A.W.G. or B&S | A.W.G. Metric |
| 0.2120 | 5 | 0.1819 | 4,621 | 0.0092 | 34 | 0.0063 | 0,1601 |
| 0.1920 | 6 | 0.1620 | 4,115 | 0.0084 | 35 | 0.0056 | 0,1422 |
| 0.1760 | 7 | 0.1443 | 3,665 | 0.0076 | 36 | 0.0050 | 0,1270 |
| 0.1600 | 8 | 0.1285 | 3,264 | 0.0068 | 37 | 0.0045 | 0,1143 |
| 0.1440 | 9 | 0.1144 | 2,906 | 0.0060 | 38 | 0.0040 | 0,1016 |
| 0.1280 | 10 | 0.1019 | 2,588 | 0.0052 | 39 | 0.0035 | 0,0889 |
| 0.1160 | 11 | 0.0907 | 2,304 | 0.0048 | 40 | 0.0031 | 0,0787 |
| 0.1040 | 12 | 0.0808 | 2,052 | 0.0044 | 41 | 0.0028 | 0,0711 |
| S.W.G. | Wire Number | A.W.G. or B&S | A.W.G. Metric | 0.0040 | 42 | 0.0025 | 0,0635 |
| 0.0920 | 13 | 0.0720 | 1,829 | 0.0036 | 43 | 0.0022 | 0,0559 |
| 0.0800 | 14 | 0.0641 | 1,628 | 0.0032 | 44 | 0.0020 | 0,0508 |
| 0.0720 | 15 | 0.0571 | 1,450 | 0.0028 | 45 | 0.0018 | 0,0457 |
| 0.0640 | 16 | 0.0508 | 1,291 | 0.0024 | 46 | 0.0016 | 0,0406 |
| 0.0560 | 17 | 0.0453 | 1,150 | 0.0020 | 47 | 0.0014 | 0,0350 |
| 0.0480 | 18 | 0.0403 | 1,024 | 0.0016 | 48 | 0.0012 | 0.0305 |
| 0.0400 | 19 | 0.0359 | 0,9119 | 0.0012 | 49 | 0.0011 | 0,0279 |
| 0.0360 | 20 | 0.0320 | 0,8128 | 0.0010 | 50 | 0.0010 | 0,0254 |
| 0.0320 | 21 | 0.0285 | 0,7239 |  | 51 | 0.00088 | 0,0224 |
| 0.0280 | 22 | 0.0253 | 0,6426 |  | 52 | 0.00078 | 0,0198 |
| 0.0240 | 23 | 0.0226 | 0,5740 |  | 53 | 0.00070 | 0,0178 |
| 0.0220 | 24 | 0.0201 | 0,5106 |  | 54 | 0.00062 | 0,0158 |
| 0.0200 | 25 | 0.0179 | 0,4547 |  | 55 | 0.00055 | 0,0140 |
| 0.0180 | 26 | 0.0159 | 0,4038 |  | 56 | 0.00049 | 0,0124 |

Wire Gauges / Gages Arranged In Columns As Follows:

AWG= American Wire Gauge, B&S= Brown & Sharpe, SWG= Imperial Standard Wire Gauge-(British legal standard)

Wire Guage /Gage Comment:

Values are stated in approximate decimals of an inch excluding the metric numbers. As a number of gauges are in use for various shapes and metals, it is advisable to state the thickness in thousands when specifying in gauge number. Metric wire gauge is 10 times the diameter in millimeters.

Call Reade first:

In review, READE is a historical manufacturer, value add custom processor, and global distributor of higher technology specialty chemical solids (metal, alloy, mineral, ceramic, composite, polymer and nanomaterials) in wire form. We welcome quoting on your wire requirements.